2021 09 14 EES RESPONSES

Group:; SP 1ST 20 ADD. Type:; Parker Water and Sanitation District 20. Status:; REVISIONS REQUIRED. Date Submitted:; 6/30/2021. Date Due:; 7/29/2021. Date Completed:; 7/15/2021 (9-7-2021 EES Responses). Reviewer:; Robert Ramsey. Notes:; 7/15/2021 10:31:24 AM Please note: 1. PWSD does not allow Fire Hydrants to exceed 100 feet in length. The scale i used shows it at 228 LF. That’s about right. Please confirm length. 2. PWSD Suggests turning the Hydrant run into a 8" Water Main with an 8" X 6" reducer to the fire hydrant. Completed. Please note this will require a 30Foot PWSD easement and a 20foot easement for the F. H. Shown. 3. Please fix the Utility legend G. does not indicate Water, E. is not for gas and so on. Completed. 4. PWSD will not allow San Service to be tied into the sampling Manhole it must be tied in down stream. Completed. 5. PWSD will not allow San Services to have bends under the Street please revise. Completed. # 26 move call out to the right location. Completed..