2021 09 14 EES RESPONSES

| Group: | SP 1ST 20 ADD |
| --- | --- |
| Type: | Parker Water and Sanitation District 20 |
| Status: | REVISIONS REQUIRED |
| Date Submitted: | 6/30/2021 |
| Date Due: | 7/29/2021 |
| Date Completed: | 7/15/2021 (9-7-2021 EES Responses) |
| Reviewer: | Robert Ramsey |
| Notes: | 7/15/2021 10:43:02 AM Please Note: Is this car wash on the same lot as the Gas Station? No. Separate Lot. Projects will be constructed at the same time, due to same owner developing the C-store and Car Wash together. Please revise plans to match this site the Fire Hydrant is not on this lot 2. Please revise the Plans to only reflect what is on this lot. Not what is going to the Gas Station. Completed. Update the Materials list. Will do. Update the Utility Legend to reflect the proper call outs. Completed. Add Sampling Manhole to the service line. Completed. Please show and call out a 2" Water Service not a 1" according to the Fixture count worksheet supplied to PWSD. Completed. Please provide Irrigation if any for review same for the Gas Station. Forthcoming. |