July 5, 2023

Robert Ramsey

Parker Water & Sanitation District

18100 E. Woodman Drive

Parker, CO 80134

RE:  	Douglas 234, Filing No. 6. Amendment 1, Lot 4 (SP22-041) – PWSD Referral Agency Comment Responses

Dear Mr. Ramsey,

Please accept this letter as our response to the 1st referral comments on the Douglas 234, Filing No. 6, Amendment 1, Lot 4 application being processed through the Town of Parker, SP22-041. Responses to comments are included in blue beneath the original comments.

- Submit a stamped Engineer’s Estimate, reflection the material list shown on page 1 of the plan set. A 20% contingency must be added to the total..

RESPONSE: An Engineer’s Estimate is provided with a 20% contingency.

- Submit an executed Standard Improvement Agreement (S.I.A.) with all required exhibits.

RESPONSE: Note. A SIA with all required exhibits is provided in this submittal.

- A letter of Credit or Cash in lieu based on the approved Engineers Estimate must be submitted prior to plan approval.

RESPONSE: Noted and we will provide prior to plan approval.

- Please provide an excel spreadsheet listing an address for each lot/building, as well as an address for irrigation. Addresses must be obtained by the Douglas County planning department.

RESPONSE: We will work on retaining the addresses for this plan.

- Please provide internal plumbing plans to PWSD. This submittal should also include a fixture count worksheet of all fixtures served by the tap.

RESPONSE: Noted. Internal plumbing plans and a fixture count worksheet is provided for this submittal.

- Please submit a complete IPP form. This is found on the www.PWSD.org website.

RESPONSE: Noted. A completed IPP form is provided for this submittal.

- Please provide completed PWSD landscape/irrigation worksheet, which can be found at Irrigation-Landscape-Worksheet-Fillable (pwsd.org).

RESPONSE: We have provided a PWSD landscape/irrigation worksheet to this submittal.

- Engineering and Landscape Review Fees must be paid before a 2nd or 3rd submittal of this project will be reviewed. This covers up to 3 reviews, subsequent reviews after that will be an additional charge at 50% the rate.

RESPONSE: Noted and we will pay the fees prior to the 3rd submittal.

- Irrigation Review Fees must also be paid before a 3rd submittal of this project will be reviewed. This covers up to 3 reviews, subsequent reviews after that will be an additional charge at 50% the rate.

RESPONSE: Noted and we will pay the fees prior to the 3rd submittal.

- All tap fees must be paid before the plans will be signed. 1.5” domestic service line and curb stop cannot be in a driveway, also tap fee for 1.5” domestic line must be paid prior to approval. Please provide address to building so that his can be invoiced. Please note you can only have a ¾” irrigation line off the domestic service.

RESPONSE: Noted. We have revised our utility layout and the 1.5” domestic service line and curb stop are not in a driveway. We are working on retaining the addresses for this plan.

- Please include necessary easement agreements. Which include a 20” fire hydrant easement, a 6” fire hydrant line must be profiled where it crosses the 24” storm drain for clearance.

RESPONSE: We have updated our utility layout with a water main into the site and provided a 30’ PWSD easement. We have profiled this main and showed the crossings of the storm drain.

- Please provide an irrigation worksheet.

RESPONSE: We have provided an irrigation worksheet to this submittal.

- Please show and call-out curb stop on 1.5” Domestic service.

RESPONSE: We have called out the curb stop on the 1.5” domestic service.

- Please show and call out 8” gate valve & tapping “T” saddle for 8” water main.

REPONSE: We have proposed a new utility layout with a water main into the site. This 8” gate valve and tapping “T” saddle is not proposed anymore.

- Please show an 8”x8”x6” Tee for the fire hydrant.

RESPONSE: We have revised the utility layout into the site and we have called out an 6”x6”x6” tee for the fire hydrant.

- There will be a Domestic Tap as well as Irrigation and invoice will NOT be provided until addresses are provided for the taps.

RESPONSE: Noted.

Please let me know if you have any questions concerning this response letter and/or the enclosed documents.

Sincerely,

RICK ENGINEERING COMPANY

Troy Bales, PE

Associate

cc:  Andrew Trietley, Ventana Capital

Enclosure