July 5, 2023

Randall Capra

Town of Parker

Fire & Life Safety

20120 Main Street

Parker, CO 80138

RE:  	Douglas 234, Filing No. 6, Amendment 1, Lot 4 (SP22-041) – Fire & Life Safety Referral Comment Responses

Dear Mr. Capra,

Please accept this letter as our response to referral comments on the Douglas 234, Filing No. 6, Amendment 1, Lot 4 application being processed through the Town of Parker, SP22-041. Responses to comments are included in blue beneath the original comments.

Development Review Division Letter (Randall Capra, Community Development Review Division)

UIC	Unresolved Issues/Comments

UIC1.	During the pre-application meetings, the applicant was informed that the concept planned submitted would not be allowed.  The applicant has created a long dead end (approximately 260’) without an approved turn-around.  This project, as submitted, is denied.

The applicant, when revisiting the site plan shall be aware that no-dead ends are allowed that exceed 150 feet; the measurement would occur from center line of the access that is perpendicular to the access road on site.

Where access cannot be provided to within 150’ of all points of the building (once an approved access is constructed, the building would be required to be sprinklered.   If this were the case, riser room would need to be located on the access side of the building and sized to accommodate the FACP (fire alarm control panel) and the fire sprinkler riser.  The domestic would be allowed to be housed in this room so long as the required clearances are provided.

This comment will serve to formalize the requirements of [21 IFC Section 503.1.1 Buildings and Facilities] where approved fire apparatus access roads shall be provided for every facility, building, portion of a building hereafter constructed or moved into or within the jurisdiction.  The fire apparatus access road shall comply with the requirements of this section and shall extend to within 150 feet of all portions of the facility and all portions of the exterior walls of the first story of the building as measured by an approved route around the exterior of the building or facility.  The center line of the fire apparatus as measured by an approved route from any point that a fire engine might park when responding to a call at this building).

This submittal does not provide for this requirement of the code.  Per the requirements of the code, the fire code official is allowed to increase the dimension of the 150 feet provided that the applicant meets Exception 1.1 of this section… “The building is equipped throughout with an approved automatic sprinkler suppression system installed in accordance with section 903.1.1, 903.1.2, or 903.3.1.3.  The applicant will need to address this issue when resubmitting.

The riser room shall be sized to accommodate the following:

- The underground fire line is not allowed to have domestic tapped off of it

- The sprinkler riser is allowed to enter no further than 24-inches into the building (and any less than 12-inches into the building).

- A three-foot clearance shall be provided in front of the riser (with 18” of clearance on either side of the riser).

- The fire alarm control panel (FACP) is required to be located on an interior wall.

- A three-foot clearance is required in front of the FACP.

- Exterior access is required to be provided into the riser room; this access shall be approved.

- Access into the building shall be provided through the riser room or immediately adjacent to the riser room.

- While domestic water can be located in the riser room, the domestic cannot be located in any way that conflicts with the access requirements for both the FACP and the sprinkler riser.

- A sidewalk is required to the riser room and a 5 x 5 pad is required in front of the FDC.

Should sprinkler be required, the applicant would be required to provide a floor plan of how the riser room is to be laid out to avoid conflicts with the site plan once the building review submittal has been made.

RESPONSE: We have updated the site plan to allow a fire apparatus to be within 150’ of all sides of the building and allow circulation around the entire site. We acknowledge that the building will require to be sprinklered. Also, we acknowledge that the riser room needs to be on the access side of the building along with being large enough.

UIC2.	The applicant shall be aware that the access road hydrant distribution was not planned to address the suppression needs for all commercial properties within this subdivision; this site requires the addition of one hydrant (to be located at the s/e corner island of the building… as required per NFPA 24 Section 7.2.3.  The hydrant shall be located within 40 feet of the building to be served.  Once a site plan, that meets the requirements of the fire code, has been deemed acceptable, the fire hydrant location will be addressed more fully.

RESPONSE: According to the 2021 IFC, which has been adopted by the Town of Parker, 1 fire hydrant of a minimum of 1,500 gpm is required to address the fire flow needs for a Type A-2 building of 1,959 sf. Also, we have revised the hydrant location to be within 40 feet of the building to be served based on the NFPA 24 Section 7.2.3 requirement.

UIC3.	The applicant shall be aware that no vertical construction on this site will be allowed until such time that curb gutter and first lift of asphalt are installed; a site inspection will be required to ensure that this requirement is made prior to allowing vertical construction to commence.

RESPONSE: We acknowledge that vertical construction will no be permitted until the first lift of asphalt is installed, and a site inspection is performed.

UIC4.	Once a site plan is provided that satisfies the intent of the code, the applicant shall provide an auto turn analysis indicating that apparatus can navigate all portions of this site.

RESPONSE: Acknowledge and we have provided an auto turn analysis. Please see the site plan sheet set for the analysis.

UIC5.	The applicant shall provide NO PARKING – FIRE LANE signage for any portion of the access where the 24-foot clear width requirement cannot be me; areas that are required to have this signage are located on both the north and sides of the building.  See below for areas highlighted in yellow:

Note - The Town of Parker requires that fire apparatus access roads meet the clear-width and weight-bearing standards of the jurisdiction in which the project is located.  Roadways shall be designed to support the imposed weight of fire apparatus, 30-ton, two axle and 40-ton, three axle vehicles.  An unimpeded clear width of 24-feet shall be maintained at all times.  As such, any location where parked vehicles would obstruct this clear width requirement will require “NO PARKING – FIRE LANE” signage.  This signage shall be red on white. Design criteria has been provided at the end of this document; ensure compliance when resubmitting.

RESPONSE: Noted.

GC	General Comments (as applicable)

GC1.	All engineering documents submitted to the Town of Parker shall bear the wet signature and seal of the engineer or architect in responsible charge of the design.

RESPONSE: We will provide signed & sealed plans with our signature set submittal.

GC2.	Water distribution and site access components shall be installed and in service prior to the construction of any portion of the structure, except by special permit issued by the Fire District.

RESPONSE: Acknowledged, the water improvements will be permitted through PWSD and we will comply with this requirement.

Please let me know if you have any questions concerning this response letter and/or the enclosed documents.

Sincerely,

RICK ENGINEERING COMPANY

Troy Bales, PE

Associate

cc:  Andrew Trietley, Ventana Capital

Enclosure