[image: image1.jpg]ParkerWater

&SANITATION DISTRICT




October 11, 2023
Rick Engineering Company

Attn:  Troy Bales
8025 West 25th Place

Lakewood, Co  80214
Re:  
Douglas 234, Filing 6, Amendment 1, Lot 4, Dunkin Donuts


2nd Review Comments, 12211 Sliceroo Drive 
Dear Mr. Bales,
Thank you for forwarding the referral request for the above-mentioned project.  After a review of the documents submitted, the Parker Water & Sanitation District has the following comments:
1) See Redlined Plans.
2) Submit a stamped Engineer’s Estimate, reflecting the material list shown on page 1 of the plan set. A 20% contingency must be added to the total.

3) Submit an executed Standard Improvement Agreement (S.I.A) with all required exhibits. 

4) A Letter of Credit or Cash in Lieu based on the approved Engineers Estimate must be submitted prior to plan approval.
5) Please provide internal plumbing plans to PWSD. This submittal should also include a fixture count worksheet of all fixtures served by the tap.
6) Please submit a complete IPP form. This is found on the www.PWSD.org website.
7) Engineering and Landscape Review Fees must be paid before a 2nd or 3rd submittal of this project will be reviewed. This covers up to 3 reviews, subsequent reviews after that will be an additional charge at 50% the rate. 

8) Irrigation Review Fees must also be paid before a 3rd submittal of this project will be reviewed. This covers up to 3 reviews, subsequent reviews after that will be an additional charge at 50% of the rate. 

9) All tap fees must be paid before plans are signed.
10) Please include necessary easement agreements.

11) Please show and call-out curb stop on 1.5” Domestic service. 

12) Please show and call out 8” gate valve & tapping “T” saddle for 8” water main.
13) Please show an 8”x8”x6” Tee for the fire hydrant.
Please let us know if you have any questions on the above comments.  We look forward to the final submittal on this project.
Sincerely,

Parker Water & Sanitation District
Robert Ramsey
Sr. Construction Inspector
Robert Ramsey








Parker Water & Sanitation District  ~  18100 E. Woodman Drive  ~  Parker, CO 80134  ~  303-841-4627


