April 27, 2023

Mr. Randall L. Capra

Town of Parker – Fire/Life Safety

20120 E. Mainstreet

## Parker, Colorado 80138

RE:	SP23-006 Crown Point F1 AMD 20 L4E – Land of Sushi

Fire Safety Submittal Comments Response

Dear Mr. Capra,

Please find below our responses to the Fire/Life Safety review comments to the Site Plan Documents facilitate your review, we have included the original comments (key issues and numbered comments) in italicized font and have provided our responses in bold.

Site Plans – Fire/Life Safety

- The applicant shall be aware that no vertical construction on this site will be allowed until such time that curb gutter and first lift of asphalt are installed; a site inspection will be required to ensure that this requirement is made prior to allowing vertical construction to commence.

Response: Acknowledged

- During the pre-application meetings, the need to provide a fire hydrant on site… this was not addressed.  A fire hydrant will be required at the s/e island by the s/e corner of the building. See the redlined drawings and the detail below for the location of the required fire hydrant.

Response: Fire hydrant has been added to the site.

3.	There are issues with the unitality; typical comments are provided below.  Ensure that the drawings address the following when resubmitting:

-	The correct Fire Life Safety signature block is provided on the correct pages; the signature block shall only be provided on the cover sheet of the Utility Plan set and the Overall Utility page.  This block can be seen at the end of this response letter.

-	The domestic is not allowed to be pulled off of the underground fire line (UFL).

-	The UFL is not allowed to share the same line as the fire hydrant.

-	The UFL is not allowed to enter any further than 24-inches into the building (and any less than 12-inches) into the building (as noted below).

-	The Utility drawings shall clearly identify the UFL by name, length and size on the plan set (a note can address this though the underground fire line itself shall also bear these notations.  The measurement shall be made from the “T” at the water main ending at the flange in the fire sprinkler control valve room.

Response: Revised to have separate lines to hydrant and to the riser room. Added UFL callout to the sheets.

4.	The overall utility plan shall be modified to address the addition of the required fire hydrant as well as relocate the UFL as shown below; address this issue when resubmitting:

Response: Items have been addressed in this submittal.

5.	The applicant has identified where the UFL is to enter the building without providing documentation as to the location of the fire sprinkler control valve room.    When resubmitting, the applicant shall provide the following information (using the redlined portion of the utility drawings shown above):

-	An exterior door shall be provided into the riser room

-	A door, either adjacent to the riser room or a door that provides immediate access into the building through the riser room shall be provided (as noted above)

-	The riser room shall be sized such that a three-foot clear space is provided around the sprinkler riser with the Fire Alarm Control Panel being located on an interior wall.  A three-foot clear space is required in front of the FACP.  A minimum of 12” is required behind the riser.

-	A sidewalk is required to be provided from the drive aisle to the riser room

-	A 5’ x 5’ concrete pad shall be provided in front of the FDC with a sidewalk provided to the FDC.

-	A detail of the riser room is required to show how the room is to be laid out (arranged), that all clearances are met, and that the exterior access has been provided into the riser room with the required access into the building.  This is a requirement and will not be allowed to be deferred.

Response:  Riser room requirements have been met with this submittal.

6.	The Town of Parker requires that fire apparatus access roads meet the clear-width and weight-bearing standards of the jurisdiction in which the project is located.  Roadways shall be designed to support the imposed weight of fire apparatus, 30-ton, two axle and 40-ton three, axle vehicles.  An unimpeded clear width of 20-feet shall be maintained at all times as well as the required 28’ clear width along the western portion of the building.  As such, any location where parked vehicles would obstruct this clear width requirement will require “NO PARKING – FIRE LANE” signage.  This signage shall be red on white. Update design criteria has been provided at the end of this document; ensure compliance when resubmitting.

Response: Heavy Duty access road to follow fire truck moving throughout the site. No Parking sign added as well.

7.	While the applicant has provided an auto turn analysis, the applicant has not addressed the access on the eastern portion of the site.  When resubmitting, the applicant shall provide an auto turn analysis indicating that apparatus can navigate all portions of this site (east side of the building); NO PARKING – FIRE LANE signage is required for any portion of the access where the 20-foot clear width requirement cannot be met.  See below for the areas required to be included in the auto turn analysis (in addition to what already has been shown) and address when resubmitting:

Response: No Fire signs added per suggestion.

8.	The items noted above with a comment number (1, 2 etc.) are items that need to be corrected to show compliance with the applicable codes. Please provide a written response to this letter indicating where the corrections are made on the plans (cloud the plans as applicable). This will speed up the review process when resubmitting.  Note – This item is listed twice to emphasize the requirement to respond to the fire life safety response letter.

Response: Refer to attached Fire Truck turning exhibit and utility plan for all changes.

Thank you in advance for taking the time to review this application.  We look forward to working with you towards approval of this development proposal.

Sincerely,

GALLOWAY

Matthew Pepin

Civil Project Engineer

matthewpepin@GallowayUS.com