Comment Review Sheet for: Les Schwab Tire Center, Douglas 234, Project # 2023-347
 Reviewed By: Robert Ramsey, Sr. Construction Inspector, PWSD (RRamsey@pwsd.org)

Engineering Comments

1. All easements must be called out and shown on the plans as well as the Plat.  The District requires single utility easements to be 30-foot exclusive PWSD easements and multiple utilities to be 50-foot non-exclusive PWSD easements (with 10-feet separation between any utility).  ALL easements must be done by separate document (on the District’s standard Easement Agreement) regardless if they are done by Plat.  20’ Hydrant Easement will be needed.
2. Trees in Right-of-ways must be a minimum of 8-feet away from any water and sanitary sewer main.  This must be called out on the Plat as well as on all construction and landscape plans.

3. There are no trees or structures, including but not limited to light poles, retaining walls and trash enclosures permitted in any Parker Water & Sanitation District easement.  Any proposed or existing structures must be clearly called out on plans.
4. A copy of the signed/recorded Final Plat must be provided to the District prior to construction plan approval.

5. Water lines in Right of Way must be under asphalt or concrete.

6. No water pipe, service, or main, shall pass through or come within 10-feet horizontally of, any part of a sewer or sewer manhole (except for 90-degree crossings).

7. The maximum distance between valves is 600-feet.

8. Submit the plumbing plans for the building(s) for verification and calculation of tap size (include engineer’s fixture count worksheet). The District uses the 2009 IPC for sizing water taps.
9. List all fittings on overall utility and plan and profile sheets with numbers (manholes, blow offs, gate valves, butterfly valves, fire hydrants, air release valves, etc. i.e., NH-GV1 or NH-MH1).

10. No more than one fire hydrant and/or 15 lots may be out of service with the closing of two or more valves.

11. A wet stamped and signed Engineers Estimate with a 20% contingency must be submitted for verification and District approval.  The approved document will be an Exhibit for the Standard Improvement Agreement and Letter of Credit.

12. Submit an executed Standard Improvement Agreement with all required exhibits.  

13. Submit completed PWSD Plan Requirements Checklist with the next submittal to ensure all plan requirements have been met.  A checklist is available online at www.pwsd.org.
14. An Industrial Waste Permit application must be completed.  Application is available at www.pwsd.org.
15. Show and call out irrigations taps and sizes on Water and Sanitary Sewer construction plans. 
16. Please Note:  the proposed 8” fire line will not be allowed as that is extremely oversized for the square footage of the building.

17. Invoices for the building and Irrigation Taps will be provided when addresses are received.

18. Invoices for Review and Inspection will be sent to you upon second review of the plans.

Landscape/Irrigation Comments

19.  PWSD will not approve a Landscape/Irrigation Plan until such plan is approved in writing/signed by the Town of Parker.

20.  Submit landscape/irrigation plans for verification and calculation of tap size(s) (include completed PWSD landscape worksheet-one worksheet per tap).  PWSD Landscape/Irrigation worksheet is available online, at www.pwsd.org/developer.html.  The approved worksheet must be shown on the approved landscaped plans.

21.  Provide a physical address for all proposed irrigation taps on the Landscape/Irrigation Worksheet in the space provided.

22. ET based Smart Irrigation Controllers with rain sensors are required on all projects.  Choose a controller from the Districts approved ET Controller list and specify the manufacturer and model number on the irrigation worksheet. www.pwsd.org/pdf/Conservation/AvailableSmartIrrigationControlTechnologies.pdf
