August 12, 2024

Avalon Bay

Andrew Johnson

RE:  	Avalon Bay

PWSD Project#:	 2024-324

TOP Etrackit#:  	 SP23-047

Andrew,

Thank you for submitting your plans for the above-mentioned project. After a review of the documents submitted, the Parker Water & Sanitation District has the following comments:

- Please see redlined plans attached.

- Please note there are no domestic meter pits for buildings, only Irrigation meter pits.

- Please number all fire hydrants and airvacs and all low point blow offs (LPBO) on plan and profile sheets.

- Please provide a license agreement for the proposed retaining wall.

- Please add LPBO’s on all water main lowering’s (see red lined plans).

- Each exhibit must have its own cover easement document.

Please let us know if you have any questions on the above comments. We look forward to the next submittal on this project.

Sincerely,

Parker Water & Sanitation District

Robert Ramsey

Robert Ramsey

Sr. Construction Inspector

Attached:  Redlined Plans