6901 South Pierce Street, Suite 315 Littleton, Colorado 80128     303-232-8088

1June 22, 2018

Mr. Alex Mestdagh, P.E.

Town of Parker Public Works Department

20120 East Mainstreet

Parker, CO 80138

SUBJECT:	Parker Pointe Response to Comments Project SUB17-05817

Dear Mr. Mestdagh,

Below I have reproduced your comment letter on the above project and added responses in red.

General Comments

- Please note that the site plans for Lots 10 and 11 were not reviewed by the Engineering Department this submittal as the site plans have not been finalized. Full submittal to follow latter.

- Per discussion with the applicant, a public improvements cost estimate will be submitted with the next referral. Cost estimate is included in the submitted materials.

- Per previous discussions with the applicant, the proposed offsite detention pond will require private agreements regarding maintenance and overall responsibility for the pond. The applicant will need to coordinate these items with the property owner, Douglas County, and the Town to ensure the arrangement is acceptable to all parties. Draft copies of agreements are tin the Towns hands for review.

- A copy of the executed access easement agreement will be required to be submitted to the Town prior to any approvals. This is under review by the parties and will be submitted upon execution.

Plat

- Show sight triangle at the access on South Parker Road. Sight triangle added to the plat.

- Ensure sight triangles are clearly called out on the plat. Called out as “Sight Triangle Easement”

- The 50’ drainage easement being shown on the plat needs to be replaced with a 50’ multi- use easement. This easement will be dedicated by the plat but PWSD will also require a 50’ multi-use easement be dedicated via separate document over the same area. Drainage easement revised to multi use easement. PWSD easements are shown to be dedicated by separate document.

Traffic Study

- Please upload the traffic study with the next submittal and ensure the comments from the previous review are addressed. Revised traffic study included.

Construction Plans

- Provide a signing and striping plan for Stroh Road. Include redirect and taper transition ratios.  The design of Stroh Road will need to be further coordinated with Town staff. Plan included as sheet C5.11. taper ratios are included on the plan.

- Please show any necessary modifications to the crosswalk and traffic signal to formalize the pedestrian crossing along the south and east legs of the Parker RD Stroh RD intersection. Crosswalk modifications shown. John Aldridge indicated that he discussed with the Town modifying the signal with a work order as opposed to a formal plan.

- Confirm western boundary of the proposed island and ensure it’s coordinated with the northern island and the adjacent thru lane. Alignment checked and confirmed.

- Please revise the dedicated right turn through the island to be 14 feet, edge of pavement to edge of pavement. Width revised. See traffic island detail on C5.16.

- Revise the site’s northeast access to align with the existing Stroh Crossing access. The Town would prefer that this access have NB thru, dedicated left, and SB thru movements. Lane alignment revised thru the intersection as requested.

- Label lane widths on signing and striping plans. Widths labeled.

- Add the Town’s Engineering signature block to the Overall Utility Plan. Signature block added.

- Some sheets still have the Town’s outdated Engineering signature block. Signature block updated.

- There was a typo on the previous review memo. The Engineering Department contact number should be 303 840 9546. Phone number revised.

- Provide cross sections for the work on Parker Road. Cross sections added as sheet numbers 5.18 thru 5.25.

- Please provide more detail on the inlet proposed at the southeast corner of Stroh and Parker. Include the existing storm sewer as well as necessary modified details on the plans. See detail on sheet 4.11.

- Please revisit the sight triangles. The distance from the curbline should be 15 feet and the corner intersection sight distance should span 555 feet along the centerline of the road for Parker RD and Stroh RD.  Ensure the sight triangles are also updated on the plat. Sight lines updated on plans and plat.

- Provide an island detail with spot elevations. See detail on 5.16.

- CDOT approval will need to be granted on the proposed curb and gutter as well as the inlets shown on Parker Road. Comment noted.

- Provide a storm sewer profile for the stub west of MH-6. See profile C sheet 4.11.

- Note that any wall over 4 feet will require a building permit. Note added to sheets 2.10 and 2.11.

- Show utility crossings on storm sewer profiles. Ensure a minimum of 18 inches of vertical separation is provided. Utility crossings added to the profiles.

- Show ramps leading into and out of the forebay per Figure 7.1 in the SDECM. Ramp added. See detail on sheet 4.91.

- Show slopes and horizontal curves of the pond access road. Ensure they comply with the geometric criteria outlined in Section 7.3.15 of the SDECM. Data added. See detail on sheet 4.15.

- Please see the attached redlines regarding the alignment of the pond maintenance access. Access road revised. I kept a little piece for turnaround.

- Access to the top of the outlet structure must be provided. Per our meeting, access to outlet structure to be provided from adjacent paved road.

- There shouldn’t be any standing water in the secondary chamber of the outlet structure. Please either lower the outlet pipe or provide concrete up to the invert of the outlet pipe. The outlet cannot be lowered. Concrete is added as indicated. See sheet 4.16, Outlet Structure detail.

- Please provide more detailed grading information for the Parker Road curb and gutter drainage. It is unclear how the road drains between Stroh Road and the site access road.  Please provide spot elevations and flow arrows/slope callouts. Spots and slopes added. Also see cross sections for proposed slopes.

- Water Quality treatment is required for the storm outfall adjacent to Parker Road. Please provide treatment calculations in the drainage report and coordinate with the design drawings. The UDFCD grass swale spreadsheet is included for treatment of this area. The swale is illustrated on the plans. An underdrain cannot be used as there is no outfall deep enough to accommodate.

- Please modify the storm pipe alignment north of the pond forebay. Change the manhole (MH – 8) to a Type C/D area inlet to drain the swale conveying flows from the north. An inlet is added at this location tying back to the manhole.

Stormwater Review Comments

The following comments concern drainage, erosion and sediment control, and non-point source pollution control issues for the subject property. They are based upon our review of the submittal documents against the criteria presented in the Town of Parker’s, Storm Drainage and Environmental Criteria Manual (SDECM), as revised, February 2014. Additional regulatory and planning documents were utilized in the review and are referenced in the comments where appropriate.

Final Drainage Report

- Include basin descriptions for all drainage basins. Additional basin descriptions are added.

- Delineate drainage basins for all areas on the site. Ensure compensatory storage is provided for basins that convey runoff off site. Additional basins are added see section V-B for compensatory discharge discussion.

- The height of the curb and allowable depth at gutter flowline in the minor event should be 6” for streets with vertical curb and gutter and 4” for streets with mountable curb. Please modify the inlet calculations accordingly. UD Inlet parameters are revised per comment.

- Please upsize inlet SR2 and clarify the drainage patterns of any bypass flows. Upon detail grading of the area, a 10’ type R is the calculated in let size in a sump condition.

- Ensure any bypass flows are accounted for in the next downstream inlet. Note that the Town only requires half of the bypass flow be included in the downstream inlet’s capacity calculations. Bypass flows are included on the UD Inlet spreadsheet.

- Please state in the drainage report that a floodplain development permit will be required for all of the proposed work in the Kinney Creek floodplain. Please provide a no-rise analysis for all of the disturbance in the floodplain including the proposed portion of the floodplain that will be filled. The hydraulic model can be obtained from the Urban Drainage and Flood Control District. The analysis will need to show the pre-project condition and the post project condition 100-year water surface elevations. The analysis needs to show no rise in the water surface elevation as proposed. Discussion of these points included in section V-D of the report. The no rise analysis is also included in the appendix.

- Please provide treatment calculations for water quality for all of the work on Parker Road. The Parker Road inlets adjacent to the site drain to a swale that may be able to be modified into a small water quality pond. The double turn lane on Southbound Parker Road will need to be addressed as well. As a suggestion, please look at the water quality volume required and determine if it will not go beyond the grassy area on the west side of the road. Grass buffer and grass swale calculations are included in the appendix.

Sediment and Erosion Control

- Add a note on all land adjacent to the project stating that no work shall occur in these areas. Note added.

- Add J-hooks to the silt fence along the north and west boundaries to limit the concentrated flows. J hooks added.

- Show TSBs and diversion ditches on the initial CBMP plan. Added to the initial plan.

- Show silt fence or sediment control log behind back of curb down- gradient of disturbed areas. SF added at back of walk along Parker Rd and Stroh Rd as well as along the east edge of the internal north south drive.

- Please include the acreage draining to the TSBs and the depth of the TSBs. TSB storage volume should be at least 3,600 cubic feet per acre of drainage area. Areas added and size of basins adjusted to achieve the 3,600 cf requirement.

Thank you for your review and comments. Please contact me if additional revisions or clarifications are required.

Professionally,

Jerry W. Davidson, P.E.

For and on Behalf of

Perception Design Group, Inc.