Town of Parker Community Development Department

Development Review Division

Attention:  Julia Duncan

Application Type:	Site Plan – Mixed Use

Status:			First Referral

Application Name:	Mainstreet and Pine Marketplace 4th AMD L4 - Mixed Use

Case/AP#:		SP23-063

Referral Received: 	August 24, 2023

Comments Due:	September 22, 2023

Application Location:	Generally located on the northwest corner of Mainstreet and PACE Center Drive.

Review date:		September 11, 2023

Plan reviewer:		Randall L. Capra, rcapra@parkeronline.org

Phone:			303.805.3163

| TOWN OF PARKER - FIRE/LIFE SAFETY: |  |
| --- | --- |

1st Submittal – Reviewed September 11, 2023

2nd Submittal – Reviewed January 28, 2024 (comments in red, italicized font)

3rd Submittal – Reviewed (comments in bold, red, italicized font)

Narrative: The applicant, Craine Architecture, is proposing a Site Plan for a 5-story (with a below grade parking garage) mixed use building with 19,000+ sq. ft. of commercial and 284 residential homes. The total building is 487,500 sf with 306,00 sf identified as muti-family residential, 12,900 sf identified as eating/drinking, 4,800 sf as retail, and 163,500 sf as parking grade and below grade parking garage.  The site is located on the northwest corner of Mainstreet and PACE Center Drive.

Code Reference: 2021 International Fire Code, 2021 International Building Code, 2020 NEC (Note – the Town of Parker will adopt the 2024 ICC codes which will be effective January 1, 2025.  Any project that comes in prior to that date i.e., December 31, 2024, will be allowed to use the 2021 ICC codes).

UNRESOLVED ISSUES/COMMENTS The items noted below with a comment number (1, 2 etc.) are items that need to be corrected to show compliance with the applicable codes. Provide a “required” written response to this letter indicating where the corrections are made on the plans (cloud the plans as applicable). This will speed up the review process when resubmitting.

- The applicant shall be aware that the subdivision infrastructure must be completed and accepted prior to starting construction for this project; examples of this infrastructure would include all utilities, fire hydrants, access roads, etc.  The applicant shall acknowledge this requirement.  Not satisfied with the second submittal; the applicant shall acknowledge that they understand this requirement and that no vertical construction will commence (either up… or down) until such time that access is provided along the west and north portions of the site (in addition to the access components already provided on the east and south portions of the site).  Address this issue when resubmitting.  Note – this requirement is consistent with our practices and the requirement has been noted with each meeting.  We work to avoid the type of conflict that Aurora experienced late last year with the podium project that is now currently under demolition as a result of the devastating fire that occurred within this structure.

- The applicant shall be aware that no vertical construction on this site will be allowed until such time that curb gutter and first lift of asphalt are installed; a site inspection will be required to ensure that this requirement is made prior to allowing vertical construction to commence.  The applicant shall acknowledge this requirement.  Not satisfied with the second submittal; the applicant shall acknowledge that they understand this requirement and that no vertical construction will commence (either up… or down) until such time that access is provided along the west and north portions of the site (in addition to the access components already provided on the east and south portions of the site).  Address this issue when resubmitting.  Note – this requirement is consistent with our practices and the requirement has been noted with each meeting.  We work to avoid the type of conflict that Aurora experienced late last year with the podium project that is now currently under demolition as a result of the devastating fire that occurred within this structure.

- The applicant shall be made aware of House Bill 23-1233 – Electrical Vehicle Charging Infrastructure in new multifamily housing.  Essentially,       this bill requires that multifamily housing comply with Article 12-115-107 of this bill for any electrical permit pulled on or after March 1, 2024.  All multifamily housing must be approved by March 1, 2024.  The applicant should plan ahead for this requirement as applicable to avoid the need to modify both building and site plan documents.  The applicant shall acknowledge this potential requirement when resubmitting.  Satisfied; the applicant has addressed this issue with the second submittal by acknowledging and indicating that the electrical engineer is in communication with Jon Nelson.

Note – the Town of Parker Senior Plans Examiner has looked at this project and has determined that should this policy stand, and should this project not meet the timeline noted in Bil 23-1233, then the proposed project would need to provide EV power transfer infrastructure for potentially up to 60% of the required parking.  Satisfied; the applicant has addressed this issue with the second submittal by acknowledging that it is their intent to meet the requirement prior to the required timeline.  The applicant shall be aware that failure to address all comments will delay the process; ensure that items #1 and #2 are addressed as required to ensure that the timeline can be met when resubmitting.

- The access on the west side of the building, while approved, is shown to have gates to be installed on the south end of the building.  A couple of things on the gates that must be acknowledged or addressed when resubmitting:  Partially satisfied; applicant addressed most of the items with the second submittal.  Items not addressed will be documented below and are required to be addressed when resubmitting.

- A separate permit is required for any gates;  gates shall not be installed until a submittal for the gates has been approved, the review fee paid, and the permit issued.

- The gates, much like an exit door, shall open in the direction of travel.  Reverse the swing of these gates.

- The gates shall have an unobstructed clear width of 20-feet provide; the site plan indicates only 13-feet of width.  Not satisfied; applicant has not addressed with the second submittal to ensure understanding.

- Gates shall be electrically operated and may be of the sing, lift or sliding type (manual gates are not allowed).

- Gates shall operate automatically with Opticom (or other approved pre-emption device).  This device shall be installed such that the gates are functional from either direction.  A Knox Key Switch (with dust cover) shall also be provided on the ingress and egress side in an approved location for emergency personnel use (locate on the passenger side of the vehicle).

- No other locks or latches shall be installed on the gates, unless specifically approved.

- Gates shall be provided with emergency power.  In the event of emergency power failure, the gates shall be open and remain open until power is restored.

- Gate placement shall not interfere with the use of fire protection equipment:  i.e. fire hydrants, fire department connections, fire sprinkler valves, etc.  Not satisfied; applicant has not addressed with the second submittal.  See bullet item below to show the location of an additional fire hydrant.

- A fire hydrant is required on each side of the gate.  Note – the fire hydrant that was discussed and previously shown on the south side of the building (at Mainstreet) appears to have been removed.  This hydrant will be required to be added back to the site plan (as will other fire hydrants) with hydrants being addressed later on within this document.  Not satisfied; applicant has not addressed with the second submittal.  Much like a standpipe in a horizontal egress, a fire hydrant is required on each side of the gate.  An additional fire hydrant is required.  See below:

- Gate placement shall not interfere with egress from the site, shall not trap people/vehicle in the site, etc.

- Emergency power shall be tested in accordance with the listing(s).  Records shall be kept on file.

- Gates shall be listed in accordance with UL 325.

Information on gate submittal requirements can be found at the end of this document.

- The pedestrian gate (or man gate) located to the east/adjacent to the vehicle access gate noted above, shall be fully accessible.  Locking hardware shall not be installed on this gate.  Address/acknowledge this issue when resubmitting.  Not Satisfied with the second submittal; while the applicant has acknowledged that egress will be provided (provided fire/panic egress hardware on this gate), the applicant has indicated that “fobbed (or accessed controlled components) will be used to secure access from the street side of the site.  The applicant shall be aware that an “access control application” is one of the required permits for this site and the building access control shall incorporate exterior access with this submittal.  Of particular note, the use of a fob is not allowed unless the applicant provides a card reader that allows the use of both a fob and a card for the reader.  In other words, a dual card/fob reader is allowed.  The applicant is allowed to use multiple card/fob keys so long as a master card key is provided for fire fighter use.  Confirm; acknowledge that a dual reader will be pursued for this project or document that a card reader will be utilized for the access control system intended for this building when resubmitting.

- Specific to the emergency response access, NO PARKING – FIRE LANE signage shall be provided on each side of the access; see below and address/acknowledge when resubmitting:  Satisfied; the applicant has addressed this issue with the second submittal by indicating that issue has been addressed and documented on the civil set.

- Based upon the information provided, it is highly likely that an emergency voice fire alarm system will be required for this project; the code analysis will help identify the requirements for this project.  Partially satisfied; the applicant has indicated that the design team is working with a fire contractor on this issue.  As an FHI, the code analysis for the building is required for site plan approval (this does not mean that issues identified with the code analysis will be required to be addressed with site plan though the general information is required prior to approval).  Note – the comment made in item number 8 shall be addressed, as well as this comment, shall be addressed prior to sign off for site plan by building.

- The applicant has not provided a sperate Overall Utility plan that addresses the locations of the require fire hydrants for this site; the location of the riser room must also be approved such that the required underground fire line can be shown on the utility drawings.  The following comments are specific to the water supply, riser room, etc.:

- The applicant has not provided code information on the construction type of the building; provide this information to ensure that the water supply shown is adequate.    Partially satisfied; the applicant has indicated that the design team is working with a fire contractor on this issue.  As an FHI, the code analysis for the building is required for site plan approval (this does not mean that issues identified with the code analysis will be required to be addressed with site plan though the general information is required prior to approval).  Note – the comment made in item number 8 shall be addressed, as well as this comment, shall be addressed prior to sign off for site plan by building.

- The applicant has not provided the required fire hydrants; during several of the pre-application meetings, the location of two additional fire hydrants was noted several times (and even shown on preliminary site plans). In the absence of a separate utility plan set, my comments are being made using the utility drawing in the Civil CD set as my point of reference.  See below a red-lined drawing with all hydrants highlighted in yellow and the two additional required fire hydrants noted in two clouded areas.  Address this issue when resubmitting.

- The location of the fire riser room shall be clearly identified on the required overall utility drawings to ensure that the location has not been changed or modified.

Note – it is noted that a fire hydrant is proposed to the right of the area shown on the site plan above.  The island identified would be a better location though I am unclear how this area will work with respect to access to the parking garage as the site plan does not appear to show anything but a curb and gutter.  Clarification on this issue would be helpful.

Along with required code analysis for the building, the applicant shall provide a floor plan of the riser room indicating  that the following conditions can be met (until the applicant provides the required information, the application will be held up… please ensure that the issue is addressed as required):  The applicant has not provided code information on the construction type of the building; provide this information to ensure that the water supply shown is adequate.    Partially satisfied; the applicant has indicated that the design team is working with a fire contractor on this issue.  As an FHI, the code analysis for the building is required for site plan approval (this does not mean that issues identified with the code analysis will be required to be addressed with site plan though the general information is required prior to approval).  Note – the comment made in item number 7, and 8 shall be addressed, as well as this comment, shall be addressed prior to sign off for site plan by building.

- An exterior door shall be provided into the riser room.

- A door, either adjacent to the riser room or a door that provides immediate access into the building through the riser room shall be provided.

- The FACP will be required to be located on an interior wall in the fire sprinkler control valve room; ensure that the riser room is sized to accommodate both the FACP and the riser.  Not satisfied with second submittal; riser room provided information on the controller (which will require three feet of clearance that has not been  provided) and has not provided room to provide the FACP on an interior wall with three feet of required clearance.

- A three-foot clearance is required in front of the FACP.  Not satisfied with second submittal; riser room provided information on the controller (which will require three feet of clearance that has not been  provided) and has not provided room to provide the FACP on an interior wall with three feet of required clearance.

- The underground shall enter the building and turn up no further than 24 inches from foundation wall; three feet of clearance is required in front of the fire riser with a minimum of 12” of clearance behind the riser and 18” to each side of the riser.

- Domestic is not allowed to tie into the underground fire line (UFL).

- Unless looped, the UFL and the hydrant are not allowed to be shared with the same dead-end water main.

- A sidewalk is required to be provided from the drive aisle to the riser room.

- A 5’ x 5’ concrete pad shall be provided in front of the FDC with a sidewalk provided to the FDC.

- A detail of the riser room is required to show how the room is to be laid out (arranged), that all clearances are met, and that exterior access has been provided into the riser room with the required access into the building.  This is a requirement and will not be allowed to be deferred.  Not Satisfied with the second submittal; the layout to include the clearances for the pump controller or the FACP.  The FACP is required to be located on an interior wall and this was not addressed.  The room likely will need to be expanded to address all code requirements.

- The location of the required fire department connection (FDC) shall be in the area of the riser room and required fire hydrant (not isolated from the riser room as currently shown).  The applicant shall provide a minimum 5-foot sidewalk from the emergency access lane to the riser room.  Address this issue when resubmitting.

- The applicant shall provide a minimum 5 x 5 pad in the area where the FDC will be located (in the area of the riser room).  Address this issue when resubmitting.

Note – while additional utilities are allowed to be located in the riser room, the additional utilities are not allowed to encroach in any of the required areas for either FACP or the riser.  This is one of the reasons why the floor plan is required.

The utility drawings shall address the following when resubmitting (reiterating some information):  Not satisfied; I received an email from the applicant’s team requesting that the fire hydrant that is located to the north of the parking garage be relocated to the south side of this entry.  Approval for the relocation of this hydrant was granted though the utility drawings indicate otherwise.  Additionally, a fire hydrant is required to be located on the north side of the vehicle gate located on the west side of the building.  Address this issue when resubmitting.

- Use the correct Fire Life Safety signature block on the cover sheet and the overall utility sheet when resubmitting; a copy of the correct signature block has been provided in the latter pages of this response letter.

- The domestic is not allowed to be pulled off of the underground fire line (UFL).

- The UFL is not allowed to share the same line as a fire hydrant.

- The UFL is not allowed to enter any further than 24-inches into the building (and any less than 12-inches into the building (as noted above) if applicable.

- The Utility drawings shall clearly identify the UFL by name, length and size on the plan set (a note can address this though the underground fire line itself shall also bear these notations.  The measurement shall be made from the “T” at the water main ending at the flange in the fire sprinkler control valve room.

- An analysis of the building for fire flow shall be provided for this project to ensure that the site infrastructure can accommodate the fire flow for a half million square foot mixed use occupancy.  This information should be used to ensure that the underground fire line is sized appropriately/correctly (ensure that the 6-inch fire line is sized appropriately).  Address this issue when resubmitting.  Not satisfied with the second submittal; the applicant shall address this issue, providing the report as required.  Address this issue when resubmitting.

- The Town of Parker requires that fire apparatus access roads meet the clear-width and weight-bearing standards of the jurisdiction in which the project is located.  Roadways shall be designed to support the imposed weight of fire apparatus, 30-ton, two axle and 40-ton three, axle vehicles.  An unimpeded clear width of 26-feet shall be maintained at all times (26-feet for buildings that exceed 30-feet in height).  The applicant has met the required 26-foot access road on all four sides of the accessible portion of the building though the applicant has not provided the required auto-turn analysis required for all projects.  This analysis shall be performed for all portions of the site including the 24-foot drive aisle provided on the s/w side of the front of the building.  Not satisfied with the second submittal; the applicant shall address this issue when resubmitting.

- Any location where parked vehicles would obstruct the clear width requirement will require specifically worded signs that state “NO PARKING – FIRE LANE” signage; directional arrows shall be indicated on both sides of the sign for all signage.  This signage shall be red on white. Update design criteria has been provided at the end of this document; ensure compliance when resubmitting.   See below for highlighted locations of required fire lane signage (additional signage may be identified once a more complete site plan has been provide or should modifications to this site plan occur):  Not satisfied with the second submittal; the applicant shall address this issue when resubmitting.

- The applicant has not provided an auto turn analysis for this site; when resubmitting, provide an analysis that shows that fire apparatus can negotiate the site.  This shall include the access on to Mainstreet.  See below for the areas that shall be included in this analysis:  Partially satisfied with the second submittal; while  the applicant did not address in the response letter, I did see that the applicant provided the required information in the civil site drawings.  For this reason, the applicant shall address all issues documented with a response letter so that I will know that you did respond as requested.

- An addressing plan for this site is required; please work with your planner and Douglas County specific to both the address and unit numbering for this project.  This issue will need to be addressed and approved prior to making a formal application for building permits as the building address will be required on all construction drawings submitted for the building permit.   Satisfied with the second submittal; the applicant noted that the address will be obtained prior to submitting the building permit.  Note – all plan sheets are required to have the building address documented on each sheet.  Work with planning and Zoning to address the suite numbering for both the commercial and residential units as only one building address shall be allowed for this building.

The items noted above with a comment number (1, 2 etc.) are items that need to be corrected to show compliance with the applicable codes. Provide a “required” written response to this letter indicating where the corrections are made on the plans (cloud the plans as applicable). This will speed up the review process when resubmitting.  Note – This item is listed twice to emphasize the requirement to respond to the fire life safety response letter.

GENERAL COMMENTS (as applicable)

All engineering documents submitted to the Town of Parker shall bear the wet signature and seal of the engineer or architect in responsible charge of the design.

Water distribution and site access components shall be installed and in service prior to the construction of any portion of the structure, except by special permit issued by the Fire District.

Underground fire lines

When thrust blocks are used as part of the pipe restraint system, submitted plans for permit shall provide detailed documentation that the thrust blocks satisfy all requirements of 19 NFPA 24: 10.8.2, including specific thrust block dimensions and mathematical calculations for block dimensions per guidelines provided in Annex A.10.8.2.

FIRE CODE REVIEW/SIGNATURE BLOCK

| All fire hydrants shall be installed according to water utility standards. The number and locations of the fire hydrants as shown on the Overall Utility Plan are correct as specified by the Town of Parker, Community Development Department. Fire Code Official or Designated Representative Date (NOTE – Underground Fire Line (UFL) submittal documents must meet the requirements of NFPA 24 when submitting for review.) |  |
| --- | --- |

FIRE ACCESS ROAD DESIGN CRITERIA

VEHICLE SPECIFICATIONS are provided for the largest apparatus in use by South Metro Fire Rescue. Fire Apparatus Access Roads shall be capable of accommodating this apparatus.

# Vehicle Specifications

Length: 47’ 9.5”

Width: 8’ 5” - (10’ 1” mirror to mirror)

Height: 10’ 9”

Wheelbase: 273 in.

Design load: 80,000 pounds Inside Cramp Angle: 40° Axle Track: 83”

Wheel Offset: 5.3”

Tread Width: 13.5”

# Turning Radii:

Inside Turn: 26 ft. 1 in. Curb to curb: 41 ft. 11 in. Wall to wall: 46 ft. 8 in.

# Where objects are present adjacent to the fire apparatus access road, particularly on turns and turn arounds which require backing, a reasonable safety margin shall be provided to prevent potential damage to the property and to the fire apparatus.

PRIVATE ROADS that provide access to more than two dwellings or one or more commercial buildings shall be constructed to meet the roadway standards approved by the South Metro Fire Rescue Authority for fire apparatus access. Private roads that do not meet the roadway standard may be accepted provided that alternative methods and materials are incorporated into the subdivision that addresses the fire and life safety of the citizens.

FIRE LANE SIGN PLACEMENT

Posting of Fire Lanes: The posting of the “Fire Lanes” is required.

3” High

¼ ” Stroke Red Letters

Fire Lane Sign Dimensions. NO PARKING – FIRE LANE signs shall be 12 inches wide and 18 inches high.

12”

18”

2 ” High 1/8 ”

Stroke

Red letters

Fire Lane Sign Characteristics: Signs shall be engineer grade reflective sheeting on 0.80 aluminum with red lettering on a white background.

Fire Lane Sign Locations. Fire apparatus access roadways between 20 and 28 feet wide, signs shall be posted on both sides. Fire apparatus access roadways between 28 feet wide and 34 feet wide, signs may be posted on one side only.

Fire Lane Sign Installation. NO PARKING – FIRE LANE signs shall be installed as follows:

- Bottom edge of the signs shall be 7 feet above surface (sidewalk) and post shall be placed 24 inches from flow line (curb).

- One sign at the beginning of the restriction (one arrow pointing towards the restriction zone).

- One sign at the end of the restriction (one arrow pointing back into restricted zone).

- One sign at least every 150 ft. within the restricted area (double arrow pointing in each direction, to indicate the continuing restriction).

- Spaced evenly within the restriction (for straight curbs/zones). For example, if the parking restriction zone is 300 ft long, only one double arrow sign is required at a distance of 150 ft. from the beginning of the restriction. If the restriction zone is 400 ft. long, two double arrow signs are required; spaced 100 ft. evenly from each other and from the beginning/ending signs.

- Spaced so that at least one readable sign is visible in front of a parked vehicle from any point along the restriction (for curved curbs/zones and areas that may present visual obstacles.)

- Set at an angle of no fewer than 30 degrees and no more than 45 degrees with the lane of traffic flow visible to approaching traffic.

- Signs shall be provided at all normal and emergency access points to structures and within 20 feet of each fire hydrant and fire department connection (FDC) in compliance with UFC 901.4.2.

- Some areas may need additional fire lane signs. Check with the Division of Life Safety for any additional requirements.

Fire Lane Sign Types. The diagrams below indicate the types of signs that may be used, and the recommended placement.

200 feet

200 feet

Additional sign styles may be used – provided the same type is used consistently.

Painting of Curbs or Streets. In addition to the required signage, South Metro Fire Rescue does permit fire lanes to be painted with curb or street markings. However, these markings shall not replace the required fire lane signs. Curbs may be painted red with 3-inch white block letters stating NO PARKING – FIRE LANE. Lettering shall be spaced every 15 feet.

Underground Fire Line - Submittal Requirements

# Reference: 2019 NFPA 24 Installation of Private Fire Service Mains and Their Appurtenances

A separate permit is required and will be issued pending review of a detailed submittal which must include the following: [21 IFC 901.2]

4.1.1 Working plans shall be submitted for approval to the authority having jurisdiction before any equipment is installed or replaced.

4.1.2 Deviation from approved plans shall require permission of the authority having jurisdiction.

4.1.3 Working plans shall be drawn to an indicated scale on sheets of uniform size, with a plan of each floor as

applicable, and shall include the following items that pertain to the design of the system:

(1) Name of owner

(2) Location, including street address

(3) Point of compass

(4) A graphic representation of the scale used on all plans

(5) Name and address of contractor

(6) Size and location of all water supplies

(7) The following items that pertain to private fire service mains:

(a) Size

(b) Length

(c) Location

(d) Material (ductile iron, PVC, etc.)

(e) Point of connection to city main

(f) Sizes, types, and locations of valves, depth at which the top of the pipe is laid below grade

(g) Method of restraint (Meg-a-Lug or similar)

(h) Stamped and signed thrust block calculations specific to the soils conditions for the site

(i) Copy of the installer’s state license

4.1.4 The working plan submittal shall include the manufacturer's installation instructions for any specially listed equipment, including descriptions, applications, and limitations for any devices, piping, or fittings. Submittals must include installation specifications for thrust blocks, corrosion protection, restraint system, bedding, detail of pipe under the building up to, and including, the flange. When it is intended that a different contractor will extend the fire line from a stopping point outside the building, to the inside flange, a second submittal and permit is required.

All plans shall be combined into a single pdf prior to uploading to the Town of Parker website.

All tees, plugs, reducers, valves, and hydrant branches shall be restrained against movement by thrust blocks [10.8.2] or restrained joint systems [10.8.3]. When thrust blocks are used as part of the pipe restraint system, submitted plans shall provide detailed documentation that the thrust blocks satisfy all requirements of Section 10.8.2, including specific thrust block dimensions and mathematical calculations for block dimensions per guidelines provided in Annex A.10.8.2.

Any individual or company who physically works on or installs any part of a fire suppression system, including underground supply lines, from public water lines to system risers and backflow preventers, must be registered with the Colorado Division of Fire Safety. [Dept. of Public Safety, Division of Fire Safety, Fire Suppression Program 8 CCR 1507-11:3.1.2] Documentation of valid annual registration is required with plan submittal.

The following website for the Colorado Division of Fire Safety will provide registration instructions.

http://dfs.state.co.us/SuppAppsProcInsp.htm

All submittals must display a wet stamp and original signature by a Colorado licensed professional engineer or NICET III, or higher, in fire suppression systems. [Dept. of Public Safety, Division of Fire Safety, Fire Suppression Program 8 CCR 1507

Vehicle Access Gates - Submittal Requirements

SUBMITTAL REQUIREMENTS

The following criteria shall be submitted prior to approval of a gate application:

An electronic submittal, provided as a single PDF, which includes:

- Locations of roads and driveways primate to the gate(s).

- Elevations and details of the gate(s) including location of gates, pedestrian gates, monuments, signs, fire hydrants, fire department connections, etc.

- Gate construction details and identification of the type of material used (wrought iron, chin link, wood, etc.).

- Location of pre-emption device (Opticom) for electrically operated gates.

- Proposed location of the KNOX Key Switches (with dust covers).

- Emergency power source.

- Product specifications sheets for gates, electrical gate controllers, and pre-emption devices.

- Any other materials necessary to ensure that the gate is designed in accordance with this standard.

Electrically operated gates:

- In the event of power failure, gates must be capable of being manually opened or provided with battery backup.

- The electrical operation that opens the gate shall be activated by:

  - An Opticom detector that opens the gate after receiving a signal from the Opticom emitter on the fire apparatus as the fire apparatus approaches the gate.

South Metro Fire Rescue uses the 3M Opticom Priority Control System, 700 Series Optical detectors. The detector, cable, and accessories must be ordered through Advanced Traffic Products, Inc. 303-604-6587

  - An approved Knox key switch that must be ordered through www.knoxbox.com 	and installed to override all entry codes (dual key access may be required depending on the law enforcement jurisdiction).

MAINTENANCE

- All gate components shall be maintained and operational at all times.

- Where more than one occupancy is served by a gate, the Fire Code Official may require that a reliable owner’s association or Metro District take responsibility for maintenance.

- Upon determining that a gate regulated by this standard is not properly maintained, the Fire Code Official may order that it be disabled or removed at the owner’s expense.